## Slide 1
Pressure Distribution in Boilers
Steam School Notes | 11 Strength of the Boiler Shell
Pressure acts perpendicular to surfaces in all directions
• Water and steam under pressure exert force equally in all directions • Force acts perpendicular to surface regardless of shape • Understanding force distribution is key to boiler strength

## Slide 2
Curved and Flat Surfaces
Steam School Notes | 11 Strength of the Boiler Shell
Cylindrical shells carry pressure more efficiently than flat plates
• Curved surfaces: Round shape carries load efficiently as tension • Flat surfaces: Pressure causes bending and bulging; bending stresses increase rapidly with size
Most boilers use curved cylindrical shapes because they resist pressure efficiently.

## Slide 3
Why Boilers Don't Fly
Steam School Notes | 11 Strength of the Boiler Shell
Internal pressure creates balanced separating forces on cylinder halves
• Pressure inside pushes upward on one half, downward on the other • Total separating force equals pressure multiplied by projected area • Upper and lower forces must match or boiler would rise

## Slide 4
Cylinder Half Forces
Steam School Notes | 11 Strength of the Boiler Shell
Pressure distribution along curved and flattened cylinder surfaces
• Circular cross-section: pressure forces balanced along semicircular arcs • Partially flattened: lower arc ADC has less length and volume than circular arc • Completely flattened: lower surface collapses to line with zero volume

## Slide 5
Shell Tension at Seam
Steam School Notes | 11 Strength of the Boiler Shell
Material along seam experiences equal opposite forces in tension
• Upper and lower forces on cylinder halves must match • Material at seam line experiences two equal opposite forces • Resisting area equals shell thickness multiplied by cylinder length on each side: 2LT

## Slide 6
Worked Example: Bursting Pressure
Steam School Notes | 11 Strength of the Boiler Shell
Calculate bursting pressure for a cylindrical shell under internal pressure
• Cylinder diameter D = 30 in, length L = 96 in, pressure P = 100 lb/in² • Total upward force: P_D = 30 × 96 × 100 = 288,000 lb • Shell thickness T = 0.250 in • Seam area: A_s = 2 × 96 × 0.250 = 48 in² • Force on seam: 288,000 ÷ 48 = 6,000 lb/in²

## Slide 7
Bursting Pressure Formula
Steam School Notes | 11 Strength of the Boiler Shell
Shell bursts when seam stress equals material tensile strength
• Bursting condition: (D·L·P_b) / (2·L·T) = σ_t • Simplified formula: P_b = (2·T·σ_t) / D • Bursting pressure independent of cylinder length
Bursting pressure depends only on shell thickness and diameter, not length.

## Slide 8
Bursting Pressure Calculation
Steam School Notes | 11 Strength of the Boiler Shell
Example calculation shows 1000 psi bursting pressure
• Given: D = 30 in, T = 0.250 in, σ_t = 60,000 lb/in² • P_b = (2 × 0.250 × 60,000) / 30 • P_b = 30,000 / 30 = 1,000 psi

## Slide 9
Tensile Failure of a Bolt
Steam School Notes | 11 Strength of the Boiler Shell
Bolt behavior under tension shows three failure stages
• Elastic stretching: material returns to original shape if load removed • Yield point: permanent deformation begins with necking • Ultimate failure: stress increases as neck narrows until fracture

## Slide 10
Ductile Material Behavior
Steam School Notes | 11 Strength of the Boiler Shell
Ductile materials deform visibly before breaking
• Necked shape on failed specimen indicates ductile material • Visible warning through significant deformation before fracture • Brittle materials show little or no necking before fracture
Boiler shells behave like ductile materials, deforming before rupture.

## Slide 11
Boiler Design Principle
Steam School Notes | 11 Strength of the Boiler Shell
Keep working stresses well below yield point for safe operation
• Metal first yields and deforms under excessive pressure • Rupture occurs at higher stress beyond yield • Design prevents rupture and keeps stresses below yield point

## Slide 12
Stress and Strain Definitions
Steam School Notes | 11 Strength of the Boiler Shell
Stress causes material deformation producing strain
• Stress: force acting on material • Strain: material deformation caused by stress • Elasticity: deformation is completely recoverable when load is removed

## Slide 13
Stress-Strain Curve Regions
Steam School Notes | 11 Strength of the Boiler Shell
Material behavior exhibits three distinct stress-strain regions
• Elastic region: low stresses, completely recoverable deformation • Yield point: material reaches yield strength and begins permanent deformation • Plastic deformation: material continues to deform until fracture
Safe operation must remain well within the elastic region.

## Slide 14
Yield and Tensile Strength
Steam School Notes | 11 Strength of the Boiler Shell
Yield strength is approximately half the tensile strength
• Yield strength: stress at which permanent deformation begins • Ultimate tensile strength: stress at which material fractures • For boiler materials: yield strength ≈ 0.5 × tensile strength

## Slide 15
Factor of Safety
Steam School Notes | 11 Strength of the Boiler Shell
Safety factor provides margin between working and failure stress
• Boilers never operated near tensile strength limit • Factor of safety (F) reduces burst pressure to safe working level • Maximum Allowable Working Pressure: P_MAWP = P_B / F

## Slide 16
MAWP Formula
Steam School Notes | 11 Strength of the Boiler Shell
Maximum allowable working pressure accounts for material strength and geometry
• P_MAWP = (2·T·σ_t) / (F·D) • Pressure depends on thickness (T), tensile strength (σ_t), factor of safety (F), and diameter (D) • Longer cylinders do not affect safe working pressure

## Slide 17
Safety Factor of Four Example
Steam School Notes | 11 Strength of the Boiler Shell
Example boiler with F=4 has 250 psi maximum working pressure
• Given: D = 30 in, T = 0.250 in, σ_t = 60,000 lb/in², F = 4 • P_MAWP = (2 × 0.250 × 60,000) / (4 × 30) • P_MAWP = 30,000 / 120 = 250 psi
Boiler bursting at 1000 psi operates safely at 250 psi with factor of safety of four.

## Slide 18
Safety Factor Relates to Yield Strength
Steam School Notes | 11 Strength of the Boiler Shell
Factor of four limits working stress well below yield point
• Factor of four working stress = σ_t / 4 • Since yield ≈ σ_t / 2, working stress ≈ half the yield strength • Operation remains in lower half of elastic range

## Slide 19
Margin for Operational Uncertainties
Steam School Notes | 11 Strength of the Boiler Shell
Safety factor provides buffer for real-world variations
• Pressure fluctuations • Material variations • Corrosion and wear • Manufacturing tolerances • Minor stress concentrations • Uncertainties in operation
Boiler operates with metal returning to original shape when load is removed.

## Slide 20
Stress-Strain Curve Graph
Steam School Notes | 11 Strength of the Boiler Shell
Stress-strain curve shows material response from elastic to fracture
Key Features • Ultimate strength • Yield strength • Fracture point • Strain hardening region • Necking region

## Slide 21
Engineering Stress Definition
Steam School Notes | 11 Strength of the Boiler Shell
Engineering stress uses original cross-sectional area in calculation
• Engineering stress: s = F / A₀ • A₀: original cross-sectional area of specimen • Formula assumes constant area during deformation

## Slide 22
True Stress and Strain
Steam School Notes | 11 Strength of the Boiler Shell
True stress accounts for decreasing area during deformation
• Specimen width and thickness decrease during stretching • Actual stress is greater than engineering stress • True stress: σ = s·(1+e) • True strain: ε = ln(1+e), where e is engineering strain

## Slide 23
Engineering vs True Stress
Steam School Notes | 11 Strength of the Boiler Shell
Engineering stress convenient for calculation; true stress represents actual state
• Engineering stress: requires only original specimen dimensions • True stress: better represents actual material state during deformation
For boiler design, allowable stress kept far below tensile strength and fracture.

## Slide 24
Factor of Safety in Boiler Design
Steam School Notes | 11 Strength of the Boiler Shell
Safety factor of four places operation safely in elastic region
• Allowable working stress kept far below ultimate tensile strength and fracture • Factor of four ensures material returns to original shape under load • Design operates safely within elastic region

## Slide 25
MAWP Design Implications
Steam School Notes | 11 Strength of the Boiler Shell
Larger diameter requires trade-offs in thickness, material, or pressure
MAWP Formula • P_MAWP = (2·T·σ_t) / (F·D)
For Larger Diameter, Choose One: • Thicker shell • Stronger material • Lower working pressure • Smaller factor of safety (if approved by code)

## Slide 26
Shell Thickness Effect
Steam School Notes | 11 Strength of the Boiler Shell
Increasing shell thickness directly increases safe working pressure
• Safe working pressure increases in direct proportion with thickness • Inverse relationship with diameter • Fundamental principle of boiler and pressure-vessel design
Shell thickness directly proportional to safe working pressure.