## Slide 1
MTRs and CRNs
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
Material Test Reports prove material; CRNs prove design
• MTR: Demonstrates material acceptability • CRN: Demonstrates design acceptability • Both may be required before component installation
An MTR and a CRN answer different compliance questions and serve complementary purposes.

## Slide 2
What Is a CRN?
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
CRN stands for Canadian Registration Number
• CRN: Issued after pressure-retaining design reviewed and accepted by applicable regulatory authority
• Valves • Fittings • Pressure vessels • Boilers • Heat exchangers • Pressure piping components
A component requiring registration may not be legally installable without an appropriate CRN.

## Slide 3
Why CRNs Exist
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
Pressure equipment failure consequences drive regulatory design review
• Serious injury • Property damage • Loss of production • Environmental damage
CRNs verify that pressure-containing designs meet code and standard requirements before service.

## Slide 4
Distinguishing MTRs and CRNs
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
MTRs and CRNs answer different compliance questions
Question | Document
Is the material acceptable? | MTR
Is the design acceptable? | CRN
• A valve may have both a valid MTR for material and a valid CRN for design • Both forms of documentation may be required

## Slide 5
Typical CRN Format
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
CRNs contain registration number and jurisdiction identifiers
• Example: 0C12345.5C • Example: 0F56789.2
• Registration number • One or more jurisdiction identifiers

## Slide 6
CRN Physical Locations
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
CRNs appear on components and supporting documentation
• Nameplate • Casting • Stamping • Manufacturer's data report • Product documentation
Examples • Pressure vessels • Safety valves • Fittings • Strainers • Heat exchangers
Both physical markings and supporting documentation should be reviewed during component inspection.

## Slide 7
Components with CRNs: Valves
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
Steam operators commonly encounter CRNs on valve designs
• Safety valves • Pressure reducing valves • Control valves

## Slide 8
Components with CRNs: Fittings
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
Fittings commonly carry CRN registration
• Forged steel fittings • Specialized branch fittings • Strainers

## Slide 9
Components with CRNs: Pressure Vessels
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
Pressure vessels regularly require CRN documentation
• Air receivers • Steam separators • Heat exchangers • Boiler components

## Slide 10
Reading a CRN
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
CRN links component design to regulatory registration records
• Does not provide material properties • Does not provide operating pressures • Acts as reference to registration records maintained by regulatory authority
CRN does not replace • MTRs • Pressure ratings • Nameplate information • Code markings
CRN supplements but does not replace Material Test Reports and other component documentation.

## Slide 11
Why Pipefitters Should Care
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
Pipefitters verify correct components during installation and inspection
• Does this component require a CRN? • Is a CRN present? • Does the documentation match the component?
Understanding CRNs helps avoid delays during inspection and certification.

## Slide 12
Common Misconception about CRNs
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
CRN proves design acceptance, not component condition
• CRN demonstrates design reviewed and accepted • Component condition must be verified by inspection, testing, and maintenance
A valve with valid CRN may still be • Worn • Damaged • Improperly installed • Unsuitable for the intended service
A CRN demonstrates acceptance of the design, not the condition of the individual component.

## Slide 13
CRN Registration Example
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
CRN issued for family of designs, not individual components
Figure
• Manufacturer • Applicable design standard • Types of valves covered • Materials of construction • Pressure ratings • Size ranges • Manufacturer model numbers
CRN registration applies to a variety of component configurations within approved scope.

## Slide 14
CRN Registration Example
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
CRN issued for family of designs

## Slide 15
What CRN Registration Covers
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
CRN applies to design configurations within approved scope
• Several sizes • Multiple pressure ratings • Different end connections
All configurations falling within approved scope are covered by same registration.

## Slide 16
What CRN Registration Does Not Cover
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
CRN does not verify material, condition, or installation
• Prove the material composition • Replace the MTR • Verify the condition of a valve • Guarantee proper installation
Material certification, inspection, testing, and maintenance address matters outside CRN scope.

## Slide 17
MTR and CRN Relationship
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
MTR proves material; CRN proves design for service acceptability
• MTR: Proves the material • CRN: Proves the design
Both MTR and CRN may be required to demonstrate pressure-retaining component acceptability.

## Slide 18
Province and Territory Suffix Codes
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
CRN suffix identifies jurisdictions accepting the design
Code | Province or Territory
1 | British Columbia
2 | Alberta
3 | Saskatchewan
4 | Manitoba
5 | Ontario
6 | Quebec
7 | New Brunswick
8 | Nova Scotia
9 | Prince Edward Island
0 | Newfoundland and Labrador
N | Nunavut
T | Northwest Territories
Y | Yukon

## Slide 19
Reading CRN Suffix Examples
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
CRN suffix order indicates registration history and jurisdiction acceptance
• 4321.5: First registered in Ontario • 4321.52: First registered in Ontario, subsequently accepted in Alberta • 4321.15: First registered in British Columbia, later accepted in Ontario
First jurisdiction shown is the original registering authority; suffix order indicates registration history.

## Slide 20
Canada-Wide Acceptance Indicator
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
Letter C indicates design accepted in all Canadian jurisdictions
• Example: 0C12877.5C • C indicates design accepted in all Canadian jurisdictions • Abbreviation used instead of listing every province and territory
Canada-wide acceptance (C suffix) streamlines CRN notation for multi-jurisdiction designs.

## Slide 21
Crane Registration CRN Example
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
Crane valve CRN 0C12877.5 shows Ontario first registration
• 0C12877.5: .5 indicates Ontario was first jurisdiction to register the design
• Upon Canada-wide acceptance, CRN shown as 0C12877.5C • C suffix indicates Canada-wide acceptance

## Slide 22
CRN Suffix Significance for Pipefitters
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
Suffix interpretation determines registration jurisdiction and scope
• Where the design was first registered • Whether the design has been accepted in multiple jurisdictions • Whether the design has Canada-wide acceptance
CRN suffix analysis is important when purchasing equipment for installation in different provinces or territories.

## Slide 23
Historical Boilers and CRNs
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
Heritage boilers often require unique individual CRN registration
• Modern valves and fittings: CRN applies to entire product family • Historical boilers: Built as individual machines with unique histories
Heritage boiler considerations • Modified over operating lives • Repaired using various methods • Constructed before modern design standards • Each may require unique registration

## Slide 24
Historical Boiler CRN and MAWP Relationship
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
CRN for historical boiler closely tied to Maximum Allowable Working Pressure
MAWP established through • Inspection • Non-destructive examination (NDE) • Thickness measurements • Engineering calculations • Applicable code requirements
As heritage boilers age, inspection may reveal condition changes affecting MAWP and registration.

## Slide 25
MAWP Reassessment for Historical Boilers
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
Periodic inspection may require MAWP recalculation and registration updates
• Corrosion, wastage, repairs affect boiler strength • NBIC requires periodic re-evaluation of historical boilers
MAWP reduction requires • Change in registered maximum allowable operating pressure • Revision of safety-valve settings • Updates to inspection records • Changes to registration documentation

## Slide 26
Historical Boiler CRN vs. Modern Components
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
Historical boiler CRN evolves through ongoing inspection and evaluation
Modern valves and fittings • CRN is primarily design-registration document
Historical boilers • CRN part of ongoing inspection and engineering evaluation • CRN may evolve as new inspection information available • CRN updated as boiler's allowable operating pressure reassessed

## Slide 27
Documentation Consistency for Historical Boilers
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
Pressure ratings, settings, and CRN must remain consistent with MAWP
• Pressure ratings • Safety-valve settings • Inspection certificates • CRN records
All documentation must remain consistent with the boiler's current MAWP.

## Slide 28
Key Takeaway: CRN Purpose and Role
Steam School Notes | 21 Canadian Registration Numbers (CRNs)
CRN proves design acceptance; MTR proves material acceptability
Canadian Registration Number demonstrates that a pressure-retaining component design has been reviewed and accepted by applicable regulatory authority, complementing Material Test Report certification for compliance and pressure equipment safety.