## Slide 1
Overview
Steam School Notes | 19 Fittings
Fittings direct flow and connect pipe sections
• Change direction • Create branches • Change pipe size • Connect or disconnect equipment • Close pipe ends
Fittings are essential components that make piping systems practical and functional.

## Slide 2
90-Degree Elbow
Steam School Notes | 19 Fittings
90° elbow changes flow direction by ninety degrees
• Commonly used where space is limited • Creates resistance to flow • Increases turbulence and pressure loss

## Slide 3
45-Degree Elbow
Steam School Notes | 19 Fittings
45° elbow produces less pressure loss than 90° elbow
• Changes direction more gradually • Reduced pressure loss compared to 90° elbow • Better for systems requiring lower resistance

## Slide 4
Long-Radius vs Short-Radius Elbows
Steam School Notes | 19 Fittings
Elbow radius affects turbulence and pressure loss
Type | Centerline Radius | Characteristics
Long-radius (LR) | 1.5 × pipe diameter | Less turbulence, lower pressure loss
Short-radius (SR) | Pipe diameter | Higher turbulence, higher pressure loss
Long-radius elbows are commonly used in steam and process piping systems.

## Slide 5
Street Elbow
Steam School Notes | 19 Fittings
Street elbow connects to fittings without intermediate pipe
• Male connection on one end • Female connection on other end • Saves space in tight installations

## Slide 6
Direction Changes Create Flow Resistance
Steam School Notes | 19 Fittings
Every elbow increases turbulence and pressure loss
• Velocity distribution changes • Turbulence increases • Pressure is lost
Piping systems should avoid unnecessary direction changes whenever practical.

## Slide 7
Tee Fitting
Steam School Notes | 19 Fittings
Tee is most common branch fitting with three openings
• Three openings in tee configuration • Branch connection equals run size • Primary branch fitting in most systems

## Slide 8
Cross Fitting
Steam School Notes | 19 Fittings
Cross provides four openings for multiple branches
• Four openings arranged in cross pattern • Allows two branch connections from single fitting • Less common than tee in typical systems

## Slide 9
Reducing Tee
Steam School Notes | 19 Fittings
Reducing tee provides smaller branch than main run
• Run: 2" • Branch: 1"

## Slide 10
Lateral Fitting
Steam School Notes | 19 Fittings
Lateral creates angled branch with smoother flow path
• Typically angled at 45° • Smoother flow path than standard tee • May reduce pressure losses

## Slide 11
Branch Connection Stresses
Steam School Notes | 19 Fittings
Branch connections experience multiple stress sources
• Internal pressure • Thermal expansion • Vibration • External loads
As pipe size and pressure increase, branch reinforcement becomes increasingly important.

## Slide 12
Changing Pipe Size
Steam School Notes | 19 Fittings
Size changes require reducers or bushings
• Size reductions accommodate changing flow rates • Choice depends on space, flow characteristics, service conditions • Bushings reduce fittings; reducers reduce pipe

## Slide 13
Bushing
Steam School Notes | 19 Fittings
Bushing threads into fitting to reduce opening size
Aspect | Details
Function | Threads into larger fitting, provides smaller opening
Example | 1" × 3/4" bushing connects 3/4" pipe to 1" fitting
Space requirement | Very compact installation

## Slide 14
Bushing Advantages and Disadvantages
Steam School Notes | 19 Fittings
Bushings offer compact installation but create stress concentration
Advantages | Disadvantages
Compact installation | Abrupt change in flow area
Lower cost | Concentrates stress in small area
Fewer fittings required | Difficult to remove after long service
Bushings are commonly used on instrument connections, drain lines, vent connections, and small auxiliary piping.

## Slide 15
Reducing Coupling
Steam School Notes | 19 Fittings
Reducing coupling joins different pipe sizes in straight run
• Joins two different pipe sizes • Examples: 1" × 3/4", 1-1/4" × 1", 2" × 1-1/2" • Stronger and more conventional than bushing

## Slide 16
Reducing Coupling Advantages and Disadvantages
Steam School Notes | 19 Fittings
Reducing couplings provide better support at cost of space
Advantages | Disadvantages
Better mechanical support | Requires more space
Easier maintenance | Adds another fitting
Commonly accepted practice | 

## Slide 17
Reducers in Welded Systems
Steam School Notes | 19 Fittings
Reducers connect different pipe sizes in welded piping
• Used in welded piping systems • Examples: 2" × 1-1/2", 4" × 3", 6" × 4" • Available in concentric and eccentric styles

## Slide 18
Concentric vs Eccentric Reducers
Steam School Notes | 19 Fittings
Reducer style selection affects flow characteristics
• Concentric: centered symmetrical reduction • Eccentric: offset reduction maintains one edge level • Choice depends on application and orientation

## Slide 19
Reducer Selection Consequences
Steam School Notes | 19 Fittings
Poor reducer selection creates flow and pressure problems
• Condensate pockets • Air traps • Increased turbulence • Water hammer conditions
Proper orientation is especially important in steam service.

## Slide 20
Coupling Fitting
Steam School Notes | 19 Fittings
Coupling joins two pipe sections in straight line
• Common in smaller piping systems • Threaded couplings most typical • Straightforward connection method

## Slide 21
Half Coupling
Steam School Notes | 19 Fittings
Half coupling creates branch when welded to vessel
• Half of a standard coupling • Commonly welded to vessels or larger pipe • Creates branch connection point

## Slide 22
Union Fitting
Steam School Notes | 19 Fittings
Union allows disconnection without rotating pipe
• Provides means of quick disconnect • Commonly used on valves, steam traps, pumps, instruments • Simplifies maintenance and replacement

## Slide 23
Why Use a Union
Steam School Notes | 19 Fittings
Union avoids removing large piping sections
• Without union, disassembly requires removing large section • Union allows quick component removal for servicing • Reduces labor and system downtime

## Slide 24
Cap Fitting
Steam School Notes | 19 Fittings
Cap fits over pipe end to close it
• Covers outside of pipe end • Provides temporary or permanent closure • Simple capping solution

## Slide 25
Plug Fitting
Steam School Notes | 19 Fittings
Plug screws into fitting to close opening
• Threads into fitting opening • Closes threaded holes • Available as hex-head or square-head styles

## Slide 26
Cap vs Plug Memory Aid
Steam School Notes | 19 Fittings
Distinguish cap and plug by where they fit
• Cap goes over a pipe • Plug goes into a fitting

## Slide 27
Threaded End Connections
Steam School Notes | 19 Fittings
Threaded connections primarily used on smaller pipe sizes
Advantages | Disadvantages
Easy to assemble | Potential leak paths
No welding required | Limited pressure and temperature capability

## Slide 28
Socket-Weld End Connections
Steam School Notes | 19 Fittings
Pipe inserted into socket and welded around outside
Advantages | Disadvantages
Strong connection | Requires welding
Suitable for higher-pressure service | More difficult to inspect internally

## Slide 29
Butt-Weld End Connections
Steam School Notes | 19 Fittings
Pipe and fitting welded directly end-to-end
Advantages | Disadvantages
Highest strength | Requires qualified welding procedures
Smooth internal bore | 
Preferred for larger steam systems | 

## Slide 30
Key Takeaway: Fittings Role
Steam School Notes | 19 Fittings
Fittings make piping systems practical and reliable
• Allow pipe to change direction • Create branches in system • Change pipe size • Connect equipment • Terminate lines
Proper fitting selection affects assembly ease, pressure capability, maintainability, and long-term reliability.

## Slide 31
Nipple Definition
Steam School Notes | 19 Fittings
Nipple is short length of pipe with threads on both ends
• External threads on both ends • Connects two threaded fittings or components • Short piece of pipe prepared for threaded service

## Slide 32
Common Nipple Uses
Steam School Notes | 19 Fittings
Nipples connect valves, instruments, and components
• Connecting valves to fittings • Extending a branch line • Installing pressure gauges • Connecting steam traps • Creating spacing between components

## Slide 33
Nipple Length Standards
Steam School Notes | 19 Fittings
Nipples available in standard lengths for different applications
• Close • Short (shoulder) • Long • Custom-cut
Exact dimensions vary by manufacturer and pipe size.

## Slide 34
Close Nipple
Steam School Notes | 19 Fittings
Close nipple has threads over entire length
• Threads cover entire length • Very little visible between fittings when assembled • Useful where space is limited • Difficult to remove because no unthreaded grip section

## Slide 35
Short Nipple
Steam School Notes | 19 Fittings
Short nipple has short unthreaded section between threaded ends
• Also called shoulder nipple • Unthreaded section visible after assembly • May provide limited wrench grip

## Slide 36
Long Nipple
Steam School Notes | 19 Fittings
Long nipple extends spacing between components
• Simply longer sections of threaded pipe • Create space between components • Bridge short distances • Position instruments or valves for easier access

## Slide 37
Barrel Nipple
Steam School Notes | 19 Fittings
Barrel nipple has threads only near ends
• Threads only at both ends • Large unthreaded section in middle • Used when greater length needed with minimal threading

## Slide 38
Running Nipple
Steam School Notes | 19 Fittings
Running nipple is threaded continuously end to end
• Threaded continuously from end to end • Similar to long close nipple • Useful when one fitting must rotate onto nipple during assembly

## Slide 39
Why Pipefitters Care About Nipples
Steam School Notes | 19 Fittings
Correct nipple length determines assembly and maintenance efficiency
• Provide wrench clearance • Allow valve handles to move freely • Improve accessibility • Simplify future maintenance
Poor nipple selection can leave components difficult or impossible to service.

## Slide 40
Nipples in Common Steam Service
Steam School Notes | 19 Fittings
Nipples frequently connect steam system components
• Between steam trap and isolation valve • Between pressure gauge and gauge valve • Between tee and drain valve • Between boiler nozzle and valve assembly • In instrument and control piping

## Slide 41
Key Takeaway: Nipples Importance
Steam School Notes | 19 Fittings
Nipple selection is important for accessibility and system layout
• Short piece of threaded pipe • Connects fittings and components • Simple in appearance but critical in function
Proper nipple selection is important for accessibility, assembly, maintenance, and overall piping layout.

## Slide 42
Flange Definition
Steam School Notes | 19 Fittings
Flange mechanically connects pipe and equipment with bolts
• Two mating flanges with gasket between • Bolts and nuts compress gasket for seal • Easily disassembled for inspection and maintenance
Flanges are ideal for equipment requiring periodic inspection or replacement.

## Slide 43
When to Use Flanges
Steam School Notes | 19 Fittings
Flanges used where equipment must be removable
• Valves • Steam traps • Pumps • Heat exchangers • Pressure vessels • Boilers
Without flanges, removing large equipment would require cutting and rewelding piping.

## Slide 44
Weld Neck Flange
Steam School Notes | 19 Fittings
Weld neck flange is preferred for many pressure applications
Characteristic | Detail
Tapered hub | Smooth transition between pipe and flange
Stress characteristics | Reduces stress concentrations
Service suitability | High pressure and temperature service
Common applications | Steam systems, process piping, high-pressure service
Weld neck flange provides excellent strength and good fatigue resistance.

## Slide 45
Slip-On Flange
Steam School Notes | 19 Fittings
Slip-on flange slides over pipe and is welded in place
Advantages | Disadvantages
Easy alignment | Lower strength than weld neck
Lower cost | More susceptible to fatigue
Simplified fit-up | 

## Slide 46
Threaded Flange
Steam School Notes | 19 Fittings
Threaded flange contains internal pipe threads
Advantages | Disadvantages
No welding required | Limited pressure and temperature capability
Convenient for small piping systems | Potential leak paths through threads

## Slide 47
Socket Weld Flange
Steam School Notes | 19 Fittings
Socket weld flange contains recessed socket for pipe
• Pipe inserted into recessed socket • Then welded in place • Used on smaller high-pressure piping

## Slide 48
Blind Flange
Steam School Notes | 19 Fittings
Blind flange is solid plate closing flanged connection
• Solid plate with no opening • Closes end of flanged connection • Used for future expansion, isolation, or testing

## Slide 49
Gaskets
Steam School Notes | 19 Fittings
Gasket compressed between flange faces creates seal
• Flange alone does not normally provide seal • Seal created by gasket compression • Material must suit system temperature, pressure, and fluid

## Slide 50
Gasket Materials
Steam School Notes | 19 Fittings
Gasket material selection affects sealing performance
• Compressed fiber • Graphite • PTFE • Spiral wound metal gaskets

## Slide 51
Gasket Selection Consequences
Steam School Notes | 19 Fittings
Improper gasket selection results in serious problems
• Steam leaks • Blowouts • Loss of pressure • Equipment damage
In steam service, gasket selection is often as important as flange selection.

## Slide 52
Flat Face Flange
Steam School Notes | 19 Fittings
Flat-face flange has completely flat sealing surface
• Completely flat sealing surface • Commonly used with cast-iron equipment • Simple sealing geometry

## Slide 53
Raised Face Flange
Steam School Notes | 19 Fittings
Raised-face flange has small raised sealing surface
• Small raised surface around bore • Most common type in industrial piping • Concentrates gasket loading for better performance

## Slide 54
Ring-Type Joint Flange
Steam School Notes | 19 Fittings
RTJ flange uses machined metal ring in precision grooves
• Metal ring seated in precision-machined grooves • Reserved for specialized applications • Very high-pressure or high-temperature service

## Slide 55
Flange Bolting
Steam School Notes | 19 Fittings
Bolts compress gasket to maintain seal
• Bolts do not directly seal; they compress gasket • Uneven tightening can damage gasket • Excessive tightening can crush gasket • Insufficient tightening causes leaks

## Slide 56
Proper Flange Tightening
Steam School Notes | 19 Fittings
Tighten bolts in crisscross pattern for even compression
• Use crisscross or star pattern • Ensures even gasket compression • Distributes load evenly around flange

## Slide 57
Flange Pressure-Temperature Ratings
Steam School Notes | 19 Fittings
Flange ratings called classes indicate pressure capability
• Class 150 • Class 300 • Class 600 • Class 900 • Class 1500 • Class 2500
Higher class generally indicates capability for higher pressure service.

## Slide 58
Flange Rating Misunderstanding
Steam School Notes | 19 Fittings
Flange class does not equal maximum psi rating
• Class 150 flange not limited to 150 psi • Rating varies with material and temperature • Actual allowable pressure from applicable standard
Flange ratings must be determined from applicable standards for specific applications.

## Slide 59
Why Pipefitters Should Understand Flanges
Steam School Notes | 19 Fittings
Proper flanged joint assembly affects system safety and reliability
• Alignment, gasket selection important • Bolting techniques critical • Pressure-class selection affects capability • Many steam leaks from incorrect assembly, not defects

## Slide 60
Key Takeaway: Flanged Connections
Steam School Notes | 19 Fittings
Flanges provide removable connection method for equipment
• Two flanges, gasket, and bolting • Understanding flange types essential • Gasket selection critical • Proper assembly practices required
Understanding flange types, gasket selection, flange ratings, and proper assembly practices is essential for steam systems.

## Slide 61
Fitting Markings Overview
Steam School Notes | 19 Fittings
Fittings marked with size, material, pressure class information
• Size markings • Material specifications • Pressure class • Manufacturing standard • Manufacturer identification
Understanding markings ensures correct fitting selection.

## Slide 62
Why Fitting Markings Matter
Steam School Notes | 19 Fittings
Identical-appearing fittings may have different ratings
• Verify size before installation • Check material specification • Confirm pressure class • Ensure manufacturing standard compliance • Wrong fitting compromises system safety

## Slide 63
Pressure Classes
Steam School Notes | 19 Fittings
Forged steel fittings marked with pressure class
• Examples: 3000, 6000, 9000 • Called three-thousand pound fitting, etc. • Not maximum allowable psi

## Slide 64
Pressure Class Misconception
Steam School Notes | 19 Fittings
Pressure class is rating category, not maximum psi
• Class 3000 not automatically 3000 psi limit • Rating depends on material • Temperature affects rating • Applicable standards determine actual pressure
Pressure class identifies fitting rating category only.

## Slide 65
Material Markings
Steam School Notes | 19 Fittings
Fittings marked with material specification
Marking | Material
A105 | Forged carbon steel for steam and process piping
A182 F304 | Forged 304 stainless steel
A182 F316 | Forged 316 stainless steel

## Slide 66
Manufacturing Standards
Steam School Notes | 19 Fittings
Fittings marked with standard to which manufactured
• Examples: B16.11, B16.9 • Standard identifies fitting type and specifications • Helps verify suitability for piping system

## Slide 67
ASME B16.11 Standard
Steam School Notes | 19 Fittings
B16.11 applies to forged threaded and socket-weld fittings
• Forged threaded fittings • Socket-weld fittings • Examples: couplings, unions, tees, elbows, bushings

## Slide 68
ASME B16.9 Standard
Steam School Notes | 19 Fittings
B16.9 applies to butt-weld fittings
• Factory-made wrought butt-weld fittings • Examples: welded elbows, reducers, tees, caps • Helps verify suitability for piping system

## Slide 69
Size Markings
Steam School Notes | 19 Fittings
Fittings marked with nominal pipe size
• Straight fittings show single size • Reducing fittings show both sizes • Examples: 1, 1-1/2, 2"; 2 × 1, 1-1/2 × 3/4

## Slide 70
Manufacturer Identification
Steam School Notes | 19 Fittings
Fitting carries manufacturer trademark or identification
• Provides product identification • Enables traceability • Supports quality-control verification • Aids in finding material certifications

## Slide 71
Heat Numbers and Traceability
Steam School Notes | 19 Fittings
Higher-grade systems use heat numbers for material traceability
• Heat number links to material test reports • Provides chemical analysis records • Includes mechanical test records • Shows material certifications

## Slide 72
Canadian Registration Numbers
Steam School Notes | 19 Fittings
CRN indicates design accepted for Canadian pressure systems
• Required for pressure-retaining components in Canada • Example marking: CRN 0C12345.5C • Regulatory authority acceptance indicator

## Slide 73
Reading Fitting Markings
Steam School Notes | 19 Fittings
Fitting markings provide multiple pieces of information
• Marking: ABC 3000 A105 1 B16.11 • Manufacturer: ABC • Pressure class: 3000 • Material: ASTM A105 forged carbon steel • Size: 1 inch • Standard: ASME B16.11

## Slide 74
Key Takeaway: Fitting Markings
Steam School Notes | 19 Fittings
Fitting markings are identification card for component
• Provide size information • Identify material • Show pressure class • Indicate manufacturing standard • Enable traceability
Learning to read fitting markings is important because many fittings appear similar even though their pressure ratings and applications may differ.

## Slide 75
Cast vs Forged Fittings Overview
Steam School Notes | 19 Fittings
Manufacturing method affects strength and capability
• Affects strength • Affects pressure capability • Affects toughness • Affects reliability • Affects suitable service applications

## Slide 76
Cast Fittings
Steam School Notes | 19 Fittings
Cast fittings poured into mold and solidified
• Molten metal poured into mold • Allowed to solidify • Materials: cast iron, malleable iron, cast steel, bronze • Complex shapes produced with minimal machining

## Slide 77
Cast Fitting Advantages
Steam School Notes | 19 Fittings
Cast fittings offer cost and manufacturing benefits
• Lower manufacturing cost • Complex shapes easy to produce • Suitable for many low-pressure applications

## Slide 78
Cast Fitting Disadvantages
Steam School Notes | 19 Fittings
Cast fittings have lower strength and reliability
• Generally lower toughness • More susceptible to casting defects • Less resistant to shock loading • Lower pressure ratings than forged equivalents

## Slide 79
Forged Fittings
Steam School Notes | 19 Fittings
Forged fittings formed by mechanical compression
• Heated metal compressed under high pressure • Metal formed by compression, not pouring • Improves grain structure and strength

## Slide 80
Forged Fitting Advantages
Steam School Notes | 19 Fittings
Forged fittings provide superior strength and reliability
• Higher strength • Better toughness • Improved fatigue resistance • Higher pressure capability • Greater reliability in severe service

## Slide 81
Forged Fitting Disadvantages
Steam School Notes | 19 Fittings
Forged fittings have cost and machining tradeoffs
• Higher cost than cast fittings • More machining may be required

## Slide 82
Visual Differences Between Types
Steam School Notes | 19 Fittings
Forged and cast fittings have distinctive appearances
Characteristic | Forged Fitting | Cast Fitting
Surface finish | Smooth machined surfaces | Rougher surface finish
Markings | Clearly stamped | Cast-in markings
Class ratings | 3000, 6000, 9000 | 125 lb, 150 lb
Appearance provides clues but markings should be used for positive identification.

## Slide 83
Forged Fittings in Steam Service
Steam School Notes | 19 Fittings
Forged steel fittings preferred for industrial steam systems
• ASTM A105 forged carbon steel fittings • ASME B16.11 threaded fittings • ASME B16.11 socket-weld fittings • ASME B16.9 butt-weld fittings
Forged fittings designed to withstand temperatures and pressures in steam service.

## Slide 84
Malleable Iron Fittings
Steam School Notes | 19 Fittings
Malleable iron common in lower-pressure utility piping
• Common in compressed-air systems • Used in water systems • Used in low-pressure utility piping • Historically used in low-pressure steam
Many industrial facilities now prefer forged steel fittings for superior strength and durability.

## Slide 85
Cast Iron Fittings in Steam Service
Steam School Notes | 19 Fittings
Cast iron fittings should be viewed cautiously in steam
• Strong in compression • Relatively brittle • Less tolerant of thermal stress • Less tolerant of mechanical shock
Cast iron fitting satisfactory in water service may not be suitable for higher-temperature steam.

## Slide 86
Typical Cast vs Forged Comparison
Steam School Notes | 19 Fittings
Same-size fittings may have vastly different capabilities
Characteristic | 110 lb Malleable Iron Elbow | 3000 lb A105 Forged Elbow
Construction | Cast | Forged
Pressure rating | Lower | Higher
Service application | Utility service | Industrial steam
Identical-appearing fittings may have vastly different operating capabilities.

## Slide 87
Why Pipefitters Should Care
Steam School Notes | 19 Fittings
Two identical-appearing fittings may differ in capability
• Verify material before installation • Check pressure class • Confirm manufacturing standard • Ensure service suitability • Never assume fitting is acceptable just because it fits

## Slide 88
Key Takeaway: Cast vs Forged
Steam School Notes | 19 Fittings
Fitting manufacturing method determines performance
• Cast and forged fittings look similar • Performance can be very different • Forged steel preferred for steam systems • Cast and malleable for lower-pressure utility
Forged steel fittings provide greater strength, toughness, and pressure capability for industrial steam applications.