## Slide 1
Pipe Markings and What They Mean
Steam School Notes | 16 Piping
Pipe markings identify material, size, and manufacturing details
• ABC PIPE • ASTM A106 GR B • ASME SA106 GR B • NPS 2 SCH 80 • SMLS • HEAT 12345

## Slide 2
Common Pipe Markings
Steam School Notes | 16 Piping
Markings identify manufacturer, specification, grade, size, schedule, method, and heat number
Term | Definition
Manufacturer Name | Identifies who produced the pipe
ASTM / ASME Specification | Identifies material standard; ASME designation adopted for pressure-retaining equipment
Grade | Identifies material grade; Grade B commonly used in steam piping
NPS (Nominal Pipe Size) | Indicates nominal pipe size such as 1", 1-1/2", or 2"
Schedule | Indicates wall thickness such as Schedule 40 or Schedule 80
Manufacturing Method | ERW (Electric Resistance Welded), SMLS (Seamless), EFW (Electric Fusion Welded)
Heat Number | Unique identifier linking pipe to steel mill production records and material test reports

## Slide 3
Why the Heat Number Matters
Steam School Notes | 16 Piping
Heat number links pipe to Material Test Report confirming compliance
• Heat number identifies unique batch of steel from production • Material Test Report (MTR) contains material properties and test results • Matching heat number to MTR verifies correct material was supplied • Inspector can confirm specification, chemical composition, and mechanical test results
Heat number is the link between physical pipe and documentation proving its compliance.

## Slide 4
Why Pipefitters Should Care
Steam School Notes | 16 Piping
Preserving pipe markings maintains material traceability
• Markings indicate size, wall thickness, material, and manufacturing method • Markings provide traceability to Material Test Report • Good shops transfer heat number to cut pieces to preserve traceability • Without markings, proving material compliance becomes difficult or impossible
Pipe markings are its identity card; preserving them is as important as making a good fit-up or weld.

## Slide 5
Schedule 40 vs. Schedule 80
Steam School Notes | 16 Piping
Outside diameter constant; schedule determines wall thickness and inside diameter
• Nominal pipe size (NPS) is a designation, not actual measurement • For given NPS, outside diameter (OD) remains constant regardless of schedule • As wall thickness increases, inside diameter (ID) decreases • Schedule 80 has thicker walls, greater pressure tolerance, and smaller flow area

## Slide 6
Common Small-Bore Pipe Dimensions
Steam School Notes | 16 Piping
Pipe dimensions vary by NPS and schedule
NPS | OD (in.) | Sch 40 Wall (in.) | Sch 40 ID (in.) | Sch 80 Wall (in.) | Sch 80 ID (in.)
1/2" | 0.840 | 0.109 | 0.622 | 0.147 | 0.546
3/4" | 1.050 | 0.113 | 0.824 | 0.154 | 0.742
1" | 1.315 | 0.133 | 1.049 | 0.179 | 0.957
1-1/4" | 1.660 | 0.140 | 1.380 | 0.191 | 1.278
1-1/2" | 1.900 | 0.145 | 1.610 | 0.200 | 1.500
2" | 2.375 | 0.154 | 2.067 | 0.218 | 1.939

## Slide 7
Internal Flow Area Reduction
Steam School Notes | 16 Piping
Schedule 80 pipe has significantly smaller flow area than Schedule 40
NPS | Sch 40 Area (in²) | Sch 80 Area (in²) | Reduction
1/2" | 0.304 | 0.234 | 23.0%
3/4" | 0.533 | 0.432 | 18.9%
1" | 0.864 | 0.719 | 16.8%
1-1/4" | 1.496 | 1.283 | 14.2%
1-1/2" | 2.036 | 1.767 | 13.2%
2" | 3.356 | 2.953 | 12.0%

## Slide 8
Flow Area Impact on Velocity
Steam School Notes | 16 Piping
Smaller flow area increases steam velocity and pressure loss
• Schedule 80 pipe carries steam 20-30% faster than Schedule 40 for same flow rate • Increased velocity results in greater pressure loss, noise, and potential erosion • 1/2" Schedule 80 carries steam about 30% faster than 1/2" Schedule 40 • 1" Schedule 80 carries steam about 20% faster than 1" Schedule 40
• V = Q / A • Reduction in area always results in increase in velocity when flow rate remains constant
A 1/2" Schedule 80 pipe has roughly 23% less flow area than a 1/2" Schedule 40 pipe; even at 2" there is about 12% reduction. Pipe schedule affects pressure rating and system performance.

## Slide 9
Threaded Pipe Connections
Steam School Notes | 16 Piping
Threaded connections created by helical grooves machined into pipe and fitting
• Threaded pipe common before welded systems became standard • Still frequently used for small-bore steam piping (2" NPS and below) • Mating threads pull components together creating pressure-tight joint • Connection tightens as pipe is screwed into fitting

## Slide 10
National Pipe Thread (NPT)
Steam School Notes | 16 Piping
NPT threads are tapered and wedge together under tightening
• Most common thread form used in North America is National Pipe Taper (NPT) • NPT threads are tapered; both male and female become narrower toward end • As connection tightens, threads wedge together creating seal • Taper approximately 1 in 16, meaning diameter changes 1 inch over 16 inches

## Slide 11
How Threads Are Cut
Steam School Notes | 16 Piping
Pipe threads cut using manual ratchet or powered threading machine
• Cut the pipe square • Ream the inside to remove burrs • Secure the pipe in the threader • Apply cutting oil • Advance the die head onto the pipe • Cut until the thread reaches proper length • Clean and inspect the threads
Properly cut thread will: • Have a smooth finish • Show no torn or flattened crests • Allow hand-tight engagement for several turns • Tighten progressively as taper engages

## Slide 12
Thread Engagement and Seal Location
Steam School Notes | 16 Piping
Seal forms along flanks of tapered threads as they wedge together
• Common misconception: seal occurs at end of pipe • Seal forms along flanks of tapered threads during tightening • Metal-to-metal contact and slight deformation produce primary seal • Thread sealants lubricate and fill microscopic leak paths

## Slide 13
Schedule 80 Threads Compared to Schedule 40
Steam School Notes | 16 Piping
Thicker walls produce deeper, stronger threads in Schedule 80
• Schedule 80 pipe develops deeper, stronger threads than Schedule 40 • More metal remains beneath thread root in Schedule 80 • Thread strength increases with thicker walls • Resistance to thread damage improves • Connection better suited to higher-pressure service
Schedule 80 threaded piping often specified where pressure, temperature, or mechanical stresses exceed Schedule 40 limits.

## Slide 14
Thread Sealants
Steam School Notes | 16 Piping
Sealants fill leak paths and lubricate threads during assembly
Thread sealants serve two purposes: • Fill spiral leak paths • Lubricate the threads during assembly
Common sealants include: • PTFE (Teflon) tape • Pipe dope (thread compound) • PTFE tape combined with pipe dope

## Slide 15
NPTF (Dryseal Pipe Thread)
Steam School Notes | 16 Piping
NPTF threads mechanically seal without tape or paste
• NPTF (National Pipe Taper Fuel) also called Dryseal pipe thread • Thread roots and crests deliberately crush and deform during tightening • Metal-to-metal deformation eliminates spiral leak path • Allows mechanical dry seal without requiring tape or paste • Lubricant still often used to ease installation

## Slide 16
Why Overtightening Is a Problem
Steam School Notes | 16 Piping
Excessive torque damages fittings and threads
• Crack cast-iron fittings • Distort valve bodies • Damage thread profiles • Make future disassembly extremely difficult
Excessive torque on threaded joints can crack cast-iron fittings and distort valve bodies.
The objective is not maximum torque; it is proper thread engagement and sealing.

## Slide 17
Galling in Threaded Joints
Steam School Notes | 16 Piping
Galling is severe adhesive wear causing metal surfaces to cold-weld together
• Galling occurs when two metal surfaces slide under pressure • Microscopic welds form between threads, then tear apart • Material transfers between threads in practical metal-to-metal seizure • Pipe dope and PTFE tape are lubricants that reduce friction and prevent galling

## Slide 18
Why Galling Occurs
Steam School Notes | 16 Piping
Galling promoted by high pressure, lack of lubrication, and soft materials
Galling promoted by: • High contact pressure • Lack of lubrication • Repeated assembly and disassembly • Similar metals rubbing together • Soft, ductile materials
Particularly common with: • Stainless-steel fasteners • Stainless threaded pipe fittings • Brass and bronze components • High-torque threaded connections

## Slide 19
What Galled Threads Look Like
Steam School Notes | 16 Piping
Galled threads appear rough, smeared, and may be impossible to turn
• Rough and torn appearance • Smeared or scored surface • Covered with metallic debris • Difficult or impossible to turn • In severe cases, threads effectively seize together

## Slide 20
Why Pipefitters Care About Galling
Steam School Notes | 16 Piping
Friction without lubrication causes thread damage and assembly problems
Without a lubricant: • More torque is required • Threads can tear or deform • Proper engagement may not be achieved • Disassembly becomes difficult years later
Thread compounds are valuable because they reduce friction, prevent galling, and allow proper thread engagement.

## Slide 21
Functions of Pipe Dope and PTFE Tape
Steam School Notes | 16 Piping
Thread sealants fill gaps, lubricate, and minimize damage during assembly
• Fill microscopic leak paths • Lubricate the threads • Reduce friction during assembly • Minimize galling and thread damage • Allow deeper thread engagement before excessive torque develops
A lubricated NPT joint typically tightens farther than a dry joint using the same wrench force, resulting in a better mechanical seal and less damage.

## Slide 22
Threaded Connections Summary
Steam School Notes | 16 Piping
Proper thread sealing requires cutting, engagement, and avoiding overtightening
• Tapered male and female threads wedge together as tightened • Threads provide mechanical strength and primary seal • Thread sealant fills microscopic leak paths • Proper thread cutting, adequate engagement, and avoiding overtightening are essential
A threaded connection seals because tapered threads wedge together, threads provide strength, and sealant fills microscopic leak paths.