## Slide 1
Main Objectives of Boiler Water Treatment
Steam School Notes | 15 Boiler Water Treatment
Five key objectives improve efficiency, safety, steam quality, and boiler life
• Prevent scale • Prevent corrosion • Control sludge • Prevent foaming and carryover • Maintain proper water chemistry

## Slide 2
Water Treatment Adjustments
Steam School Notes | 15 Boiler Water Treatment
Sodium carbonate addresses most water chemistry problems
• High hardness: add sodium carbonate • Low pH: add sodium carbonate • Low alkalinity: add sodium carbonate • High TDS: perform blowdown
Retest boiler water after treatment to ensure all parameters remain within desired ranges

## Slide 3
Minimal Low-Cost Monitoring Kit
Steam School Notes | 15 Boiler Water Treatment
Four tests cover most important water chemistry indicators
• pH strips • Hardness test strips • Alkalinity test kit • TDS/conductivity meter
• Scale prevention • Corrosion prevention • Sludge control • Carryover control • General water chemistry control

## Slide 4
Water Hardness
Steam School Notes | 15 Boiler Water Treatment
Hardness minerals precipitate during heating and form insulating scale
• Water hardness is concentration of dissolved calcium and magnesium salts in water
• Scale acts as insulator, reducing heat transfer and increasing fuel consumption • Severe scale formation leads to overheating of boiler metal and reduced boiler life • Hardness reported in parts per million (ppm) as CaCO₃

## Slide 5
Measuring Hardness
Steam School Notes | 15 Boiler Water Treatment
Test strips or titration kits measure hardness levels
• Hardness test strips: immerse in water sample and compare with colour chart • Titration-based kits provide more accurate results than test strips

## Slide 6
Interpreting Hardness Results
Steam School Notes | 15 Boiler Water Treatment
Classification ranges guide treatment decisions for traction boilers
0–50 ppm | Low hardness
50–100 ppm | Moderate hardness
100–200 ppm | High hardness
Above 200 ppm | Very high hardness
Lower hardness reduces scale formation and chemical treatment needs

## Slide 7
Hardness Treatment with Sodium Carbonate
Steam School Notes | 15 Boiler Water Treatment
Sodium carbonate converts hardness minerals into removable sludge
• Reacts with dissolved calcium salts and converts to calcium carbonate sludge • Sludge removed by blowdown rather than remaining as hard scale • Reduces scale-forming hardness • Increases alkalinity • Raises pH
Retest boiler water after sodium carbonate treatment to confirm all parameters remain in range

## Slide 8
pH in Boiler Water
Steam School Notes | 15 Boiler Water Treatment
Mildly alkaline pH between 9 and 11 prevents corrosion and foaming
• Low pH increases corrosion risk • Excessively high pH contributes to foaming and other problems • Easily measured with pH test strips or meter
If pH too low, add sodium carbonate and retest

## Slide 9
pH vs Alkalinity
Steam School Notes | 15 Boiler Water Treatment
pH and alkalinity are different but related water chemistry controls
• pH measures how alkaline the water is • Alkalinity determines reserve capacity to stay alkaline when conditions change
pH measures current condition; alkalinity measures resistance to change

## Slide 10
Shelf Analogy: pH and Alkalinity
Steam School Notes | 15 Boiler Water Treatment
pH determines height on shelf; alkalinity determines shelf width for buffering
• Wide shelf (high alkalinity): acidic contamination causes small pH change • Narrow shelf (low alkalinity): same contamination causes large pH drop • Alkalinity acts as chemical buffer, absorbing acid effects before significant pH change

## Slide 11
Buffering Chemistry
Steam School Notes | 15 Boiler Water Treatment
Hydroxide, carbonate, and bicarbonate ions neutralize incoming acids
• H⁺ + CO₃²⁻ → HCO₃⁻ • H⁺ + HCO₃⁻ → H₂CO₃ • Buffering continues as long as enough buffering species remain

## Slide 12
Sodium Carbonate Effects
Steam School Notes | 15 Boiler Water Treatment
Washing soda raises pH and increases alkalinity simultaneously
• Makes water more alkaline (raises the shelf) • Makes that alkalinity more resistant to change (widens the shelf)

## Slide 13
Alkalinity Endpoint
Steam School Notes | 15 Boiler Water Treatment
Endpoint reached when water's buffering capacity is fully consumed
• Titration is a method of chemical measurement in which reagent of known concentration is added to a sample until a defined endpoint is reached
• pH meter method: endpoint at approximately pH 4.5 • Methyl orange indicator method: colour change from yellow to orange-red at approximately pH 4.5 • Volume of acid required indicates water's buffering capacity

## Slide 14
Alkalinity Test Kit Procedure
Steam School Notes | 15 Boiler Water Treatment
Commercial kits use titration with indicator to measure buffering capacity
• Sample treated with indicator, then titrated with standardized acid solution • Endpoint identified by colour change • Number of drops converted directly to ppm as CaCO₃ • Process identical to laboratory titration method

## Slide 15
Determining Alkalinity
Steam School Notes | 15 Boiler Water Treatment
Practical target range for steam traction boiler is 100–300 ppm as CaCO₃
• Below 100 ppm: limited buffering capacity, rapid response to contamination • Above 300 ppm: increased risk of foaming, carryover, elevated dissolved solids

## Slide 16
Alkalinity Calculation
Steam School Notes | 15 Boiler Water Treatment
Titration volume and acid normality determine alkalinity value
• Formula: A = (Vₐ · N · 50000) / Vₛ • A = alkalinity; Vₐ = volume acid; N = normality acid; Vₛ = volume sample • Simplified for 100 mL sample with 0.02 N acid: A = Vₐ · 10 • Greater acid volume required indicates greater alkalinity and buffering capacity

## Slide 17
Alkalinity Test Kit Equipment
Steam School Notes | 15 Boiler Water Treatment
Standard components needed to perform alkalinity testing
• Alkalinity test kit • Clean sample container • Boiler-water sample • Measuring cylinder or test tube supplied with kit

## Slide 18
Alkalinity Testing Procedure
Steam School Notes | 15 Boiler Water Treatment
Eight steps measure boiler-water alkalinity using commercial test kit
• Collect representative boiler-water sample and cool to room temperature • Fill test tube with sample volume specified in kit instructions (50 mL or 100 mL typical) • Add indicator drops as specified in kit instructions (typically 2 to 5 drops) • Gently mix sample to distribute indicator • Add standard acid reagent one drop at a time while swirling sample after each drop • Continue adding acid until indicator changes colour permanently (endpoint at pH ~4.5) • Record total number of drops or volume of acid required to reach endpoint • Convert to alkalinity using manufacturer's conversion factor or formula

## Slide 19
Calculating Alkalinity from Test Results
Steam School Notes | 15 Boiler Water Treatment
Test kit acid drops convert directly to alkalinity ppm using calibration factor
• Kits calibrated so drops convert directly to alkalinity value • Conversion factor supplied by manufacturer • Based on acid concentration, sample size, and drop volume • Some kits: each drop equals fixed value (e.g., 10 ppm as CaCO₃) • Other kits: drop count converted to volume before applying formula

## Slide 20
Total Dissolved Solids (TDS)
Steam School Notes | 15 Boiler Water Treatment
TDS meter estimates dissolved solids concentration from electrical conductivity
• Pure water is poor electricity conductor • Dissolved minerals and salts form ions that carry electrical current • Increased ion concentration increases conductivity • TDS reported in parts per million (ppm)

## Slide 21
Sources of TDS in Boilers
Steam School Notes | 15 Boiler Water Treatment
Treatment chemicals and minerals accumulate in boiler water as pure water evaporates
• Sodium carbonate (Na₂CO₃) • Sodium sulfate (Na₂SO₄) • Sodium chloride (NaCl) • Calcium salts • Magnesium salts • Various boiler-treatment chemicals
As steam is produced, pure water leaves boiler while dissolved solids remain, increasing concentration

## Slide 22
TDS Monitoring and Blowdown
Steam School Notes | 15 Boiler Water Treatment
Rising TDS indicates accumulation requiring blowdown to remove concentrated water
• Rising TDS reading indicates dissolved salts accumulating in boiler water • Excessive TDS contributes to foaming, carryover, and solids deposition • Blowdown removes portion of concentrated boiler water • Fresh feedwater replaces blown-down water • TDS baseline established and trends monitored over time
TDS provides general indication of water concentration rather than specific chemical concentration

## Slide 23
Summary: Four-Parameter Water Treatment Program
Steam School Notes | 15 Boiler Water Treatment
Simple testing routine using four measurements maintains optimal boiler-water quality
Measurement | Purpose | Typical Action
Hardness | Detect scale-forming minerals | Add sodium carbonate
pH | Detect corrosion risk | Add sodium carbonate
Alkalinity | Measure buffering capacity | Add sodium carbonate
TDS | Measure concentration of dissolved solids | Blow down boiler
Regular monitoring of these four values minimizes scale, corrosion, foaming, and carryover