## Slide 1
Chapter Summary: Injector Fundamentals
Steam School Notes | Chapter 16: Injector Fundamentals
Injector operation and design principles
• Injectors force water into boilers against boiler pressure using steam momentum with no moving mechanical parts • Operation relies on converting pressure into momentum in steam, transferring momentum to water, then recovering it as pressure • Three-stage system: steam nozzle expands steam to high velocity, combining cone mixes and condenses steam with water, delivery cone recovers pressure • Design varies by pressure rating: low-pressure injectors (15–80 psi) tolerate cold water and dirt; high-pressure injectors (125–300+ psi) require precise conditions but deliver higher efficiency • Operating sensitivities include correct steam pressure, adequate water supply, clean internal passages, proper feedwater temperature, and absence of air leaks on suction side

## Slide 2
How an Injector Works
Steam School Notes | Chapter 16: Injector Fundamentals
Injector mechanism and pressure-to-momentum conversion
• Injector: A device that uses steam from the boiler to force water into the boiler against boiler pressure, with no moving mechanical parts
Operating Principle • Steam expands through a nozzle to very high velocity (hundreds of m/s), creating a jet that carries significant momentum • High-velocity steam jet entrains cold water and condenses upon contact with it • Condensation collapses the enormous steam volume, transferring momentum to water • Combined jet enters a diffuser (delivery cone) where velocity is converted back into pressure • Final pressure exceeds boiler pressure, forcing water into the boiler
Why Simple Connection Fails • A gauge glass connecting steam and water spaces at equal pressure produces no motion because it transmits only pressure • An injector manufactures momentum through deliberate pressure-to-velocity conversion in the steam nozzle, then recovers it as pressure in the delivery cone

## Slide 3
Comparative Velocities: Steam vs. Water
Steam School Notes | Chapter 16: Injector Fundamentals
Velocity differences and energy conversion between steam and water
Steam Velocity • At 100–150 psig: 300–500 m/s at nozzle exit • Saturated steam specific volume: ~0.2–0.3 m³/kg • Speed of sound: ~450–500 m/s • Steam is compressible: pressure drop causes expansion and acceleration to sonic velocity (choked flow) • High velocity provides the momentum needed to entrain feedwater
Water Velocity • Liquid water is effectively incompressible • Pressure drop does work directly on water mass, converting pressure energy into kinetic energy • Typical velocity from boiler water space: tens of metres per second (approximately 40 m/s at 8 bar pressure difference) • Lower velocity results because mass density that must be accelerated is much higher than steam
Key Difference • Although steam and water escape at very different speeds, both experience the same boiler pressure • Steam supplies high velocity through compressible expansion; water accepts transferred momentum and recovers pressure • Injector exploits this difference in response to pressure drop

## Slide 4
Internal Injector Components and Flow Path
Steam School Notes | Chapter 16: Injector Fundamentals
Penberthy injector anatomy and water delivery mechanism
Figure
Internal Components • Steam inlet: supplies steam from boiler dome or wagon top • Converging steam nozzle: accelerates steam to high velocity • Combining cone: location where steam entrains water and begins to condense • Delivery cone: accelerates mixed jet and converts velocity to pressure toward boiler • Overflow passages: route for excess water or steam during startup • Overflow valve assembly (K): priming and safety system
Operating Flow • High-velocity steam from nozzle creates vacuum that draws water in from suction side • Water mixes with steam in combining cone • Condensation restores pressure balance • Mixed jet forced through delivery cone into boiler • Overflow valve vents excess during startup

## Slide 5
Boiler System Integration
Steam School Notes | Chapter 16: Injector Fundamentals
Injector circuit and plumbing configuration
Diagram
Circuit Components • Steam supply from dome or wagon top with isolation valve • Injector with steam throttle, water throttle and overflow check • Inlet with inspection tee, isolation valve, check valve, and cheater
Circuit Function • Steam supplied from dome or wagon top through isolation valve to injector • Injector throttles and mixes steam with water • Overflow check diverts unstable flow during startup • Stable flow directed through boiler inlet check valve into boiler • Inspection tee allows visual confirmation of water delivery

## Slide 6
Overflow Check Valve: Priming and Control
Steam School Notes | Chapter 16: Injector Fundamentals
Overflow valve operation during startup and steady-state conditions
Overflow Valve Function • Safety and priming system for the injector • Lets water and steam escape when injector is not yet 'picked up' • Automatically closes once injector begins delivering water to boiler • Reopens if injector loses pickup during operation
Startup Sequence: Valve Opens • Steam valve opened: high-velocity steam shoots through steam nozzle, creating partial vacuum in combining cone • Vacuum draws water from suction side, but condensation is incomplete and pressure in delivery cone is below boiler pressure • Overflow valve remains open: pressure in combining and delivery cones is below atmospheric or oscillating and cannot lift boiler check valve • Excess steam, uncondensed steam, water slugs, or air escape through overflow passages, producing 'spitting' or 'overflowing' sound • Without open overflow valve, injector cannot prime
Pickup and Closure: Valve Closes • Condensation becomes complete as water flow stabilizes • Steam jet condenses completely inside combining cone, collapsing steam volume • Mixture accelerates through delivery cone, converting velocity into pressure • Injector transitions from 'spitting' to 'working' • Pressure in delivery cone rises above atmospheric pressure • Overflow valve is pushed shut by pressure differential • All flow directed toward boiler check valve • Injector becomes silent and smooth; overflow valve acts as check valve preventing backflow
Loss of Pickup: Valve Reopens • If condensation process is interrupted, pressure in delivery cone collapses • Causes include: water supply falters, steam pressure fluctuates, scale or debris disrupts jet, operator throttles incorrectly • Overflow valve reopens, injector begins 'spitting' again • Operator knows instantly that injector has dropped out • Prevents boiler pressure from forcing water backward through injector

## Slide 7
Overflow Valve: Extreme Conditions
Steam School Notes | Chapter 16: Injector Fundamentals
Overflow valve behavior under fault conditions
Valve Stuck Closed at Steam Opening • Circuit from steam to water becomes closed loop, similar to a gauge glass • No flow results because pressures equalize and forces balance • No mechanism exists to convert pressure into net momentum without open overflow
Flow Continuation After Valve Closure • Boiler check valve opens and overflow check valve closes when internal pressure exceeds atmospheric • At this point, injector is no longer a steam jet device but a pure water pump powered by the collapse of steam volume • Pumps do not need an open discharge to atmosphere to continue flow

## Slide 8
Condensation as the Power Source
Steam School Notes | Chapter 16: Injector Fundamentals
Role of steam condensation in pressure recovery
Condensation Inside Combining Cone • Steam jet condenses into the water stream • Steam's enormous volume collapses suddenly • Momentum is conserved during collapse • Mixture pressure rises sharply
Consequence • Injectors can deliver water above boiler pressure • This high-pressure delivery is why injectors overcome boiler back-pressure • Condensation collapse is the fundamental power source
Connection to Boiler Heating • Same physics governs rapid pressure rise when boiler reaches boiling point • Steam has enormous specific volume; accelerates to extreme velocities during formation • Condensation collapses that volume; pressure is recovered from velocity • Boiler's rapid pressure rise during boiling is the inverse phenomenon

## Slide 9
Operating Sensitivities and Dependencies
Steam School Notes | Chapter 16: Injector Fundamentals
Factors affecting injector performance and reliability
Critical Operating Requirements • Correct steam pressure: must be within injector design range to maintain proper jet velocity • Adequate water supply: suction-side supply must be available to prevent air entry • Clean internal cones: scale or debris disrupts steam jet geometry and condensation • Proper feedwater temperature: excessive heat reduces condensation efficiency; too hot causes injector to fail • No air leaks on suction side: disrupts water flow and prevents proper vacuum formation
Physics Foundation • All sensitivities trace back to same fundamental physics: steam velocity, condensation, and momentum transfer • Any condition that disrupts these three elements will cause injector failure or erratic operation

## Slide 10
Low-Pressure Injectors: Design and Application
Steam School Notes | Chapter 16: Injector Fundamentals
Characteristics and operating range of low-pressure steam injectors
Typical Pressure Range • ~15–80 psi; sometimes up to ~100 psi depending on design
Design Characteristics • Larger steam nozzle • Larger combining cone • Larger water passages • Gentler cone angles
Operating Advantages • Easy starting at low pressure • Tolerant of cold feedwater • Tolerant of minor scale or dirt • Less sensitive to adjustment
Limitations • Inefficient at high pressure • Tendency to overflow above design pressure
Typical Applications • Early locomotives • Traction engines • Stationary boilers • Systems with slowly rising boiler pressure

## Slide 11
High-Pressure Injectors: Design and Application
Steam School Notes | Chapter 16: Injector Fundamentals
Characteristics and operating range of high-pressure steam injectors
Typical Pressure Range • ~125–300+ psi; design dependent
Design Characteristics • Smaller steam nozzle • Tighter combining cone throat • Sharper delivery cone geometry • More precise internal dimensions
Operating Advantages • High efficiency at rated pressure • Smooth delivery at high boiler pressure • Minimal steam waste once running
Limitations • Difficult or impossible to start at low pressure • Sensitive to warm feedwater • Sensitive to scale or dirt • Sensitive to incorrect nozzle sizing
Typical Applications • Later steam locomotives • High-pressure stationary boilers • Marine boilers • Systems with steady operating pressure

## Slide 12
Low-Pressure vs. High-Pressure Injectors: Comparison
Steam School Notes | Chapter 16: Injector Fundamentals
Feature comparison and selection criteria for injector types
Feature | Low-Pressure Injector | High-Pressure Injector
Starting pressure | Very low | Moderate to high
Steam nozzle size | Large | Small
Dirt/scale tolerance | High | Low
Feedwater temp tolerance | Good | Poor
Efficiency at pressure | Lower | Higher
Ease of starting | Easy | Difficult
Pressure Range Terminology • Term 'low-pressure' and 'high-pressure' refer to the boiler steam pressure range the injector can work over, not the pressure delivered to the boiler • Low-pressure injectors designed to start and operate with ~15–80 psi • High-pressure injectors designed to operate efficiently at ~125–300+ psi

## Slide 13
Common Locomotive Practice and Pressure Range
Steam School Notes | Chapter 16: Injector Fundamentals
Dual injector configurations and geometry-determined pressure ranges
Two-Injector Configuration • Two injectors often fitted to locomotives • Low-pressure injector for starting and low-pressure operation • High-pressure injector for efficient running at road pressure
Pressure Range is Fixed by Geometry • Injector pressure range cannot be changed by valve adjustment • Pressure range is fixed by internal geometry: steam cone diameter, combining cone throat, delivery cone shape • Changing pressure range requires changing nozzles, not valve adjustment