## Slide 1
What Valves Do
Steam School Notes | 18 Valves
Valves control fluid flow in piping systems
• Pipe carries fluid • Fittings direct it • Valves control it
• Start, stop, regulate, direct flow • Isolation and throttling • Pressure control and reverse-flow prevention • Overpressure protection

## Slide 2
Selecting the Right Valve
Steam School Notes | 18 Valves
Valve function determines performance capability
• On-off valve performs poorly for throttling • Regulation valve damaged if used as stop valve • Each valve type has specific purpose and limitations
Understanding the purpose and limitations of each valve type is essential for anyone working with steam systems.

## Slide 3
Basic Valve Components
Steam School Notes | 18 Valves
Most valves contain the same fundamental parts
Component | Function
Body | Main pressure-retaining component; contains flow passage and piping connections
Bonnet | Covers valve body and supports stem
Stem | Transfers motion from handwheel or actuator to closure element
Seat | Sealing surface against which closure element closes
Disc, Plug, or Ball | Closure element that blocks, permits, or regulates flow
Packing | Prevents leakage around moving stem; adjustable for wear

## Slide 4
Valve Position Indication
Steam School Notes | 18 Valves
Visible position indication improves safety and prevents errors
• Operators must determine open, closed, or partial position • Many designs provide visible indication • Prevents operating errors during maintenance and isolation

## Slide 5
Quarter-Turn Valve Handles
Steam School Notes | 18 Valves
Handle orientation directly indicates closure element position
• Found on ball valves and plug valves • Handle perpendicular to pipe = valve closed • Handle parallel to pipe = valve open
Advantage • Immediate visual verification of position • Quick determination from distance

## Slide 6
Rising-Stem Valves
Steam School Notes | 18 Valves
Exposed stem length indicates valve opening
• Found on gate valves and globe valves • Stem moves outward as valve opens • Exposed stem length shows approximate opening
Advantages • Easy visual confirmation of position • Position determinable from distance

## Slide 7
Non-Rising-Stem Valves
Steam School Notes | 18 Valves
Stem rotates without moving outward during operation
• Stem does not change position as valve opens • Operator relies on handwheel position or indicators • Used where headroom is limited

## Slide 8
Position Indicators
Steam School Notes | 18 Valves
Dedicated indicators provide reliable position verification
Indicator Types • Pointer plates • Mechanical indicators • Colored markers • Electrical limit switches
Common Applications • Actuated valves • Motor-operated valves • Control valves • Remote-operated valves

## Slide 9
Why Valve Position Matters
Steam School Notes | 18 Valves
Operating incidents often result from incorrect position assumptions
• Many incidents occur when valve position is misjudged • Before starting equipment, verify the actual position
Verification Steps • Identify the correct valve • Confirm intended position • Verify actual position visually
Never assume a valve is open or closed based solely on previous operation or labeling.

## Slide 10
Screwed Bonnet Design
Steam School Notes | 18 Valves
Bonnet threads directly into valve body
• Bonnet threads into body • Simple and economical design • Common on smaller valves
Disadvantage • Limited wrenching surface • May become difficult to remove after years at elevated temperatures

## Slide 11
Union Bonnet Design
Steam School Notes | 18 Valves
Union nut provides larger wrenching surface for disassembly
• Body screws into bonnet • Union nut secures assembly • Larger wrenching surface than screwed bonnet
Advantage • Greater mechanical advantage during disassembly • Easier to dismantle after years of service

## Slide 12
Why Bonnet Design Matters
Steam School Notes | 18 Valves
Thermal cycling and periodic maintenance require careful disassembly
• Steam valves operate at 400°F (200°C) or higher • Repeated heating-cooling cycles tighten threaded components
Periodic Disassembly Required For • Inspection • Cleaning • Seat maintenance • Packing replacement • Long-term layup

## Slide 13
Service-Friendly Valve Selection
Steam School Notes | 18 Valves
Maintenance ease affects long-term value and reliability
• Consider maintenance requirements alongside operating performance • Valve easy to inspect and repair provides advantages • Especially important in steam applications with periodic inspection
Experienced Operators Prefer • Union-bonnet design for service-friendliness • Particularly on regularly inspected or thermally cycled valves

## Slide 14
Five Primary Valve Functions
Steam School Notes | 18 Valves
Each valve type serves a specific control purpose
• Isolate flow • Regulate flow • Prevent reverse flow • Control pressure • Protect equipment from overpressure
• Some valves perform multiple functions • Every valve designed with primary purpose in mind

## Slide 15
Isolation Valves
Steam School Notes | 18 Valves
Designed for fully open or fully closed service
• Isolation valves control on-off flow • Primary function is complete flow blocking or allowing • Three main types: gate, ball, plug

## Slide 16
Gate Valves
Steam School Notes | 18 Valves
Wedge gate moves perpendicular to flow path
Characteristics • Excellent isolation • Low pressure drop when open • Poor throttling performance
Advantages • Minimal flow restriction • Good shutoff capability
Disadvantages • Slow operation • Damage risk when partially open
Gate valves should be either fully open or fully closed.

## Slide 17
Ball Valves
Steam School Notes | 18 Valves
Quarter-turn rotation of drilled sphere controls flow
Advantages • Quick operation • Excellent shutoff • Compact design
Disadvantages • Not ideal for precise flow control
• Most common valves in modern steam systems • Quarter-turn rotates ball between fully open and closed

## Slide 18
Plug Valves
Steam School Notes | 18 Valves
Tapered or cylindrical plug with drilled passage controls flow
• Quarter-turn operation similar to ball valves • Used where quick operation and positive shutoff required • Flow passage drilled through tapered or cylindrical plug

## Slide 19
Globe Valves
Steam School Notes | 18 Valves
Disc moves toward or away from seat to regulate flow
Advantages • Excellent throttling capability • Good flow control • Reliable operation
Disadvantages • Higher pressure drop • More tortuous flow path
• One of most common throttling valves • Frequently used where steam flow must be adjusted

## Slide 20
Angle Globe Valves
Steam School Notes | 18 Valves
Globe valve function with 90-degree flow direction change
Advantages • Good throttling capability • Eliminates need for separate elbow • Compact installation
Disadvantages • Higher pressure drop than straight-through valves
• Combines valve and elbow into single component • Reduces number of fittings required

## Slide 21
Globe Valve Flow Direction
Steam School Notes | 18 Valves
Pressure should enter beneath disc and seat for optimal performance
When Pressure Acts Beneath Seat • Valve operation requires less force • Stem packing experiences less pressure • Valve is easier to control • Wear is reduced
• Globe valves usually marked with flow-direction arrow • Must be installed per manufacturer recommendations

## Slide 22
Y-Valves (Y-Globe Valves)
Steam School Notes | 18 Valves
Angled seat and stem reduce pressure loss while maintaining shutoff
Advantages • Lower pressure drop than standard globe valve • Excellent resistance to wire drawing and erosion • Well suited to high-temperature service • Self-cleaning design
Common Applications • Boiler blowdown lines • Continuous blowdown systems • High-pressure steam service

## Slide 23
Needle Valves
Steam School Notes | 18 Valves
Needle-shaped closure element enables precise flow control
• Specialized form of globe valve • Needle-shaped closure element • Enables extremely precise flow control
Common Applications • Instrument connections • Gauge lines • Sampling systems

## Slide 24
Valve Selection for Flow Regulation
Steam School Notes | 18 Valves
Gate valves unsuitable for throttling service
Partially Open Gate Valve Risks • Vibration • Erosion • Seat damage
• Common mistake is using gate valve to throttle flow • For flow regulation, use globe or needle valve

## Slide 25
Check Valves
Steam School Notes | 18 Valves
Automatically prevent reverse flow without operator action
• Allow flow in one direction only • Prevent reverse flow automatically • No operator action required • Must be installed with flow arrow pointing correctly

## Slide 26
Swing Check Valve
Steam School Notes | 18 Valves
Hinged disc swings open with forward flow and closes on reversal
• Hinged disc swings open with desired flow direction • Disc closes against seat when flow reverses

## Slide 27
Lift Check Valve
Steam School Notes | 18 Valves
Vertical moving disc lifts with forward flow and seats on reversal
• Flow lifts disc from seat • Reverse flow forces disc back onto seat

## Slide 28
Why Check Valves Matter
Steam School Notes | 18 Valves
Reverse flow causes equipment damage and system upset
Reverse Flow Consequences • Equipment damage • Pump damage • Water hammer • Process upset
• Check valves installed downstream of pumps • Critical equipment protection

## Slide 29
Pressure Reducing Valves (PRVs)
Steam School Notes | 18 Valves
Automatically reduce high inlet pressure to controlled outlet pressure
• Lowers higher inlet pressure to lower outlet pressure • Example: 150 PSI steam supply reduced to 30 PSI • Widely used in steam distribution systems
Benefits • Improved safety • More efficient equipment operation • Better process control
• PRVs do not provide overpressure protection • Separate safety valve may be required downstream

## Slide 30
How a Safety Valve Works
Steam School Notes | 18 Valves
Spring force holds disc closed until system pressure overcomes it
• Remains closed during normal operation • Calibrated spring holds disc against seat • As pressure rises, upward force increases
• At set pressure, force overcomes spring • Disc begins to lift • Valve pops open rapidly at full lift
• Opens rapidly rather than gradually • Allows full flow to relieve excess pressure • Reseats only after pressure falls below set point

## Slide 31
Blowdown in Safety Valves
Steam School Notes | 18 Valves
Intentional pressure difference prevents rapid cycling and chatter
• Blowdown is pressure difference between opening and closing • Allows sufficient pressure drop before reseating • Example: Set at 150 psi, reseats at approximately 147 psi
• Without blowdown, valve repeatedly opens and closes • Rapid cycling called chatter • Chatter causes excessive seat wear and reduced reliability
• Properly functioning valve opens quickly • Remains open long enough to relieve excess pressure • Reseats only after sufficient pressure drop

## Slide 32
Safety Valve Key Concepts
Steam School Notes | 18 Valves
Set pressure, blowdown, and chatter define valve behavior
• Set Pressure: Pressure at which valve begins to open • Blowdown: Difference between opening and reseating pressure • Chatter: Rapid repeated opening and closing from unstable conditions

## Slide 33
Why Safety Valves Are Critical
Steam School Notes | 18 Valves
Final line of defense against dangerous overpressure
Without Overpressure Protection • Boilers may be damaged • Pressure vessels may fail • Piping systems may rupture
• Safety valves are most important protective devices • Never isolate from equipment without approved procedures
Safety valves should never be isolated from the equipment they protect unless specific approved procedures are followed.

## Slide 34
Safety Valve Set Pressure Determination
Steam School Notes | 18 Valves
Set pressure determined by Maximum Allowable Working Pressure
• Set pressure not selected arbitrarily • Determined by equipment Maximum Allowable Working Pressure (MAWP) • Prevents equipment exposure to excessive pressure
For Historical Boilers, MAWP Determined By • Non-destructive examination (NDE) • Inspection of material condition • Measurement of remaining thickness • Engineering calculations using boiler formulae
A safety valve must not be adjusted above the MAWP of the equipment it is intended to protect.

## Slide 35
Safety Valve Adjustment and Sealing
Steam School Notes | 18 Valves
Certified adjustment and sealing provide assurance of set pressure
• Set pressure adjusted and certified by qualified technicians • Adjustment performed under approved quality assurance program • Valve sealed after testing to show integrity
• Seal provides assurance pressure remains certified • Broken or missing seal requires valve removal and reinspection • Under normal conditions, modern boiler safety valve rarely operates
• Frequent lifting usually indicates operating problem • May indicate pressure control issue or valve sizing problem

## Slide 36
Historical Boiler Operation and Safety Valves
Steam School Notes | 18 Valves
Modern MAWP may be lower than original design pressure
• Steam traction engines operate differently from modern boilers • Inspections and engineering assessments may determine lower MAWP • Operators may work near safety-valve set pressure during normal operation
Example Scenario • Traction engine driving sawmill • Steam demand suddenly decreases while boiler producing steam • May experience occasional safety-valve operation
• Frequent operation affects valve reseat ability • Increases wear on seating surfaces

## Slide 37
Pop Valve Regulation in Historical Boilers
Steam School Notes | 18 Valves
Antique pop valve regulated pressure while protecting government safety valve
• Some jurisdictions permitted antique pop valve as regulating device • Pop valve set to open at lower pressure than certified safety valve • Allowed pressure control without repeatedly lifting safety valve
Valve Roles • Pop valve: Regulating device for normal operation • Government valve (safety valve): Final overpressure protection • Government valve only operates if regulator fails
• Term government valve reflects official certification role • Certified safety valve is ultimate overpressure protection device

## Slide 38
Safety Valve Key Takeaway
Steam School Notes | 18 Valves
Safety valve is final overpressure defense based on equipment MAWP
• Safety valve is protective device, not regulating device • Set pressure determined by equipment MAWP • Final line of defense against overpressure
A safety valve is the final line of defense against overpressure. It is a protective device, not a pressure-regulating device, and its set pressure is determined by the MAWP of the equipment it protects.

## Slide 39
Automatic Gauge Glass Valves
Steam School Notes | 18 Valves
Ball checks restrict flow if gauge glass breaks
• Found in water-column and gauge-glass installations • Contain small ball checks in flow passage • Normally remain clear during operation
• If gauge glass breaks, sudden flow increase causes ball to seat • Restricts or stops steam and water discharge • Provides additional protection during glass failure
• Additional protection measure, not sole isolation • Manual shutoff valves must remain accessible

## Slide 40
Valve End Connections
Steam School Notes | 18 Valves
Different connection types suit different piping applications
Connection Type | Application
Threaded | Common on smaller piping systems
Socket-Weld | Frequently used for small-bore high-pressure service
Butt-Weld | Common on larger industrial piping systems
Flanged | Used where equipment may require removal or maintenance

## Slide 41
Valve Ratings and Markings
Steam School Notes | 18 Valves
Standard markings identify valve specifications and suitability
Typical Markings Include • Manufacturer • Size • Material • Pressure class • Flow direction (where applicable) • CRN (where applicable)
• Markings verify valve suitability for intended service • Example: 2", 150 class, A216 WCB • Example: 1", 800 class, A105

## Slide 42
Reading Valve Markings
Steam School Notes | 18 Valves
Interpret standard valve markings to verify suitability
Example Marking: ABC / 2 / 300 / A216 WCB • Manufacturer: ABC • Size: 2 inch • Class: 300 • Material: Cast carbon steel (A216 WCB)
• Valve markings important for quality control • Enable traceability of valve specifications • Similar to pipe and fitting markings

## Slide 43
Valve Installation Verification Checklist
Steam School Notes | 18 Valves
Verify critical specifications before installing any valve
Before Installing a Valve, Verify • Size • Material • Pressure class • Flow direction • Intended function
• Valves expensive and critical piping components • Proper selection and installation affect safety and performance • Never assume interchangeability based on pipe size alone
Never assume two valves are interchangeable simply because they have the same pipe size.

## Slide 44
Chapter 18 Key Takeaway
Steam School Notes | 18 Valves
Valve selection and operation essential for system safety and reliability
• Different valve types designed for different functions • Functions include isolation, throttling, reverse-flow prevention, pressure control, and overpressure protection • Understanding each valve's operation and application critical
• Essential for safe and reliable steam system operation • Proper selection prevents equipment damage and personnel hazards • Improves overall system performance and safety
Valves control the flow of fluids within a piping system. Different valve types are designed for different functions, including isolation, throttling, reverse-flow prevention, pressure control, and overpressure protection. Understanding how each valve operates and where it should be used is essential for safe and reliable steam system operation.