## Slide 1
Chapter Overview
Steam School Notes | Chapter 14: Properties of Water and Steam
Energy requirements and thermodynamic foundations for boiler operation
A steam engine requires ~800,000 kJ of energy to reach working pressure from cold start
This energy is comparable to 3–4 large modern EV battery packs (60–80 kWh each)
Eight core quantities form the backbone of boiler physics: mass, volume, temperature, pressure, energy, power, specific heat, and specific volume
Steam-table values enable accurate calculation of thermodynamic properties at any pressure or temperature
Three distinct physical stages describe the warm-up process: heating to 100 °C, boiling at constant temperature, and pressurization
Boiler warm-up is a sequence of sensible thermodynamic steps with predictable energy requirements at each stage.

## Slide 2
Core Quantities in Steam Work
Steam School Notes | Chapter 14: Properties of Water and Steam
Eight physical quantities that underpin all boiler calculations
Mass
  Amount of water or steam
Volume
  Water space, steam space, tender, wagon
Temperature
  Sensible heat, saturation temperature
Pressure
  Boiler pressure, steam-table lookup
Energy
  Heat added or removed
Power
  Rate of heat transfer
Specific Heat & Latent Heat
  How water stores energy
Specific Volume
  Why small steam masses fill large spaces

## Slide 3
Units: SI and Imperial Systems
Steam School Notes | Chapter 14: Properties of Water and Steam
Unit systems for mass, volume, temperature, pressure, and energy
Mass: kilogram (kg) or pound-mass (lb)
Volume: liter (L), cubic meter (m³), gallon (US gal), cubic foot (ft³)
Temperature: Celsius (°C), kelvin (K), Fahrenheit (°F), Rankine (°R)
Pressure: kilopascal (kPa), bar, pounds per square inch (psi)
Energy: joule (J), kilojoule (kJ), megajoule (MJ), British thermal unit (BTU)
Power: watt (W), kilowatt (kW), BTU/h, boiler horsepower (BHP)
Gauge pressures (PSIG) are referenced to local atmospheric pressure; absolute pressures are referenced to a perfect vacuum
Temperature differences use K or °R; °C and °F cannot be mixed directly
1 BHP = 33,475 BTU/h = 9.81 kW
1 BTU = 1055.056 J

## Slide 4
Specific Heat and Latent Heat
Steam School Notes | Chapter 14: Properties of Water and Steam
How water stores energy as sensible heat and latent heat
Specific Heat
  Energy required to raise 1 kg by 1 K; SI units: kJ/(kg·K)
  Governed by: Q = m·c·ΔT
Latent Heat of Fusion
  Energy required when a solid changes phase to liquid; water: 334 kJ/kg at 0 °C
Latent Heat of Vaporization
  Energy required when a liquid changes phase to vapor; water: 2257 kJ/kg at 100 °C
Specific Heat by Material and Phase
Material | Phase | Specific Heat | Temperature Range
Water | Solid (ice) | 2.1 kJ/kg·°C | < 0 °C
Water | Liquid | 4.18 kJ/kg·°C | 0–100 °C
Water | Gas (steam) | 2.0 kJ/kg·°C | > 100 °C
Steel | Solid | 0.49 kJ/kg·°C | < 1500 °C
Steel | Liquid | 0.80 kJ/kg·°C | ~1500–2800 °C
Steel | Gas (vapor) | 1.0 kJ/kg·°C | > 2800 °C

## Slide 5
Specific Volume and Density
Steam School Notes | Chapter 14: Properties of Water and Steam
Why small steam masses occupy large volumes
Specific Volume (v)
  Volume occupied by 1 kg of substance; SI units: m³/kg
  Inverse of density; thermodynamics uses specific volume for cleaner equations
At low pressure, steam is 'fluffy'—large volume per kg
At high pressure, steam is denser—smaller volume per kg
The ratio vg/vf (steam volume to liquid volume) is hundreds to thousands, explaining why pressure rises rapidly when steam fills a fixed volume
Pressure rise only begins after the steam space is full; sensible heating precedes latent-heat generation

## Slide 6
Steam Tables: Core Concepts
Steam School Notes | Chapter 14: Properties of Water and Steam
How to read and apply steam-table data
Steam tables give thermodynamic properties of water and steam at different temperatures and pressures
Tables are built on three core ideas: saturation (liquid-vapor boundary), phase (liquid, vapor, or mixture), and property sets (values for energy and volume calculations)
Saturation tables: use when water is boiling (T and P linked)
Superheated tables: use when steam is hotter than saturation temperature
Compressed water tables: rarely needed in boiler work
Reading a Saturated Steam Table
Convert gauge pressure to absolute by adding 101.3 kPa (14.7 psi)
Find the row for your pressure or temperature
Read vf, vg, hf, hfg, hg from the table (subscripts f and g denote fluid and gas)
For wet steam (quality x): h = hf + x·hfg and v = vf + x·(vg − vf)
Common mistake: using gauge pressure instead of absolute pressure
Latent heat (hfg) decreases at higher pressure because liquid and vapor properties converge
Specific volume of steam (vg) increases with temperature and decreases with pressure

## Slide 7
Saturation Curve: Temperature and Pressure
Steam School Notes | Chapter 14: Properties of Water and Steam
How saturation temperature depends on pressure
Saturated steam is steam in equilibrium with liquid water at a given pressure
Saturation temperature is fixed by pressure; boiling water stays at 100 °C at 1 bar
If pressure increases on boiling water, the boiling point rises: at 2 bar water boils at ~120 °C; at 10 bar at ~180 °C
The relationship is monotonically increasing and logarithmic in form
Engineering approximation: Tsat(P) ≈ 100 + 35.4·ln(P) for reasonable accuracy over 1–10 bar range
Latent Heat Approximation
  Hv(P) ≈ 2257 − 2.3·(Tsat(P) − 100) [kJ/kg]
  Decreases at higher pressure; approaches zero near the critical point
Specific Volume Approximation
  Vv(P) ≈ 0.004·(Tsat(P) + 273) / P [m³/kg]
  Derived from ideal gas law; captures T/P dependence of steam volume

## Slide 8
Boiler Warmup: Piecewise Function
Steam School Notes | 14 Properties of Water and Steam
Boiler transitions through heating, boiling, and pressurization regimes
Each stage has distinct energy requirements and physical meaning.

## Slide 9
Piecewise Boiler Warm-Up Model: Stage 1
Steam School Notes | Chapter 14: Properties of Water and Steam
Heating water and steel from ambient to 100 °C (1 bar)
Energy range: 0 ≤ q < q₁
All heat goes into raising temperature of water and steel shell
No boiling; no pressure rise
Required energy: q₁ = Cwarm·(100 − T₀) where Cwarm = mw·cw + ms·cs
Physical meaning: heat applied to large thermal mass, no steam produced, no pressure rise, temperature increases linearly
Example: 100 kg of water heated from 20 °C to 100 °C requires ~33 MJ; at 50 kW firing rate, ~11 minutes
Take-away: before boiling, the boiler is sluggish—lots of heat, slow temperature rise, almost no pressure

## Slide 10
Piecewise Boiler Warm-Up Model: Stage 2
Steam School Notes | Chapter 14: Properties of Water and Steam
Boiling at constant temperature to fill steam space at 1 bar
Energy range: q₁ ≤ q < q₂
Temperature stops rising once water reaches 100 °C
All additional heat converts liquid water into steam to fill steam space
Required energy: Δq = (Vs / vv(1)) · Hv(1)
Physical meaning: temperature stays at 100 °C while 1-bar steam fills the steam space; pure latent heat with no temperature change
At 1 bar, steam is very 'fluffy' (large vv), so total mass is small and Δq is brief
The model produces only a narrow energy interval between sensible heating completion and pressure-rise onset

## Slide 11
Piecewise Boiler Warm-Up Model: Stage 3
Steam School Notes | Chapter 14: Properties of Water and Steam
Pressurization by heating to saturation temperature at Pset
Energy range: q₂ ≤ q < q₃
After steam space is filled at 1 bar, further heat does two things:
a) Sensible heating: Cwarm·[Tsat(Pset) − 100] raises temperature of water, steel, and existing steam
b) Additional steam generation at higher pressure: (Vs / vv(Pset))·Hv(Pset) provides extra steam mass at the higher pressure
Physical meaning: pressure rises only after steam space is full; everything heats to the higher saturation temperature; extra steam mass required at that pressure is generated
At higher pressure, steam is denser, so the same steam space contains more mass
Both sensible heating and latent-heat generation occur simultaneously during pressurization

## Slide 12
Piecewise Boiler Warm-Up Model: Stage 4
Steam School Notes | Chapter 14: Properties of Water and Steam
Final state at operating pressure
Energy range: q ≥ q₃
Boiler is full of saturated steam at Pset
Water and steel are at Tsat(Pset)
Boiler is ready for work
Temperature stays fixed at saturation temperature; no further temperature rise
Once q₃ is reached, adding more heat does not increase temperature—only pressure (if the boiler is sealed) or produces additional steam (if a valve is open)
This is the steady-state operating condition for a hot-standby boiler

## Slide 13
Worked Example: Boiling a Kettle
Steam School Notes | Chapter 14: Properties of Water and Steam
Applying sensible-heat calculations to an everyday problem
Steps to Calculate Heating Time
Identify known quantities: m = 2.0 kg, T₀ = 20 °C, Tf = 100 °C, ΔT = 80 K, c ≈ 4.18 kJ/(kg·K), Q̇ = 2.0 kW
Compute energy required: Q = m·c·ΔT = 2.0 × 4.18 × 80 ≈ 670 kJ
Convert energy and power to time: t = Q/Q̇ = 670 / 2.0 ≈ 335 s ≈ 5.5–6 minutes
Result: with a 2.0 kW kettle, heating 2.0 kg of water from 20 °C to 100 °C (no losses) takes ~5.5–6 minutes
This structure applies directly to boiler calculations, with the difference that m is hundreds of kilograms and Q̇ comes from fuel consumption and boiler efficiency

## Slide 14
Raising Pressure in a Sealed Boiler
Steam School Notes | Chapter 14: Properties of Water and Steam
How pressure rises when the steam space is sealed and being heated
Once boiling begins, temperature and pressure follow the saturation curve
The entire water mass must be heated from Tsat(0 psig) to Tsat(Ptarget)
Required sensible heat: Qpressurize = m·c·[Tsat,target − Tsat,initial]
Latent heat contributes a small amount because the steam space contains very little mass: ms = Vsteam / vg(P)
Increasing firing rate increases Q̇, reducing time required to raise pressure despite large energy requirement
Time to raise pressure: t = Q / Q̇
At the same firing rate, time from 0 psig to 100 psig is similar to warm-up time (~1.5–2 hours for a 25 BHP boiler)

## Slide 15
Heat Transfer Stages: Cold Water to Working Pressure
Steam School Notes | Chapter 14: Properties of Water and Steam
Four distinct thermodynamic regimes in boiler operation
Four Stages of Boiler Heating
Heating Before Boiling
  All heat raises temperature of liquid water; high heat capacity (c ≈ 4.18 kJ/kg·K); slow, predictable rise; pressure barely changes
Reaching the Boiling Point (0 psig)
  At 100 °C (212 °F), water reaches saturation at atmospheric pressure; temperature and pressure become locked to saturation curve
Heating During Boiling (Two-Phase Region)
  Added heat converts liquid to steam; no significant temperature rise; steam occupies hundreds of times liquid volume; pressure must rise in sealed volume
Time to Raise Pressure
  Raising pressure from 0 psig to 50 psig requires only ~48 °C (86 °F) of temperature rise but large latent heat; this stage is faster than pre-boil warm-up

## Slide 16
Worked Example: 25 BHP Traction Boiler Warm-Up (Phase 1)
Steam School Notes | Chapter 14: Properties of Water and Steam
Calculating energy and time to reach first boil from cold start
Boiler specification: 250 gal (946 kg) water capacity; 250 ft² heating surface; initial temperature 20 °C (68 °F); target first boil at 100 °C (212 °F)
Boiler steel mass: 1613 kg; total thermal mass requires warming through 80 K
Energy for water: Qw = 1082.4 kg × 4.18 kJ/(kg·K) × 80 K ≈ 362 MJ
Energy for steel: Qs = 1613.1 kg × 0.49 kJ/(kg·K) × 80 K ≈ 63 MJ
Total required: Q₁ ≈ 425 MJ
Observed warm-up time: ~2 hours to 'lift the pin' (reach first steam)
Net power requirement: 425 MJ / 7200 s ≈ 59 kW (at the water/steel, not at the fuel)
Wood fuel (35% boiler efficiency): 121 kg (267 lb) of wood for Phase 1
Practical burning rate: ~150 lb/h, producing approximately 300 lb total wood consumption to first boil

## Slide 17
Worked Example: 25 BHP Traction Boiler Warm-Up (Phase 2)
Steam School Notes | Chapter 14: Properties of Water and Steam
Calculating energy and time to raise pressure from 0 psig to 100 psig
After boiling begins, temperature must rise from 100 °C (212 °F) to 170 °C (338 °F) at 8 bar (≈100 psi)
Sensible heat for water: Qw = 1082.4 kg × 4.18 × 70 K ≈ 333 MJ
Sensible heat for steel: Qs = 1613.1 kg × 0.49 × 70 K ≈ 58 MJ
Latent heat for steam generation (0.335 m³ steam space): Qsteam ≈ 3.1 MJ
Total Phase 2 requirement: Q₂ ≈ 394 MJ (similar to Phase 1 despite shorter temperature rise, because latent heat dominates)
Time to pressurize at same 59 kW net power: ~1.9 hours
Dominant energy requirement: 70 °C temperature rise of entire water mass
Latent-heat component is relatively small compared to sensible heating of water and steel
Total warm-up time from cold to 100 psi: ~4 hours at steady firing

## Slide 18
Boiler Volumes and Mass: Calculation Methods
Steam School Notes | Chapter 14: Properties of Water and Steam
Geometric decomposition for determining water space, steam space, and boiler steel mass
Water Space
  Volume occupied by liquid water in boiler
Steam Space
  Volume above water line, occupied by steam; calculated as circular segment projected along cylinder axis
Total boiler volume = (barrel + wrapper + dome) − (firebox + flues)
Steam space volume calculated from circular segment: known radius, perpendicular height from water line, cylinder length
Water space volume = total volume − steam space volume
Boiler steel mass calculated from plate areas × thickness × steel density
Example 25 BHP boiler: total 50 ft³, steam space 11.8 ft³, water space 38.2 ft³ (238 gal), steel mass 3556 lb (1613 kg)